## Slide 1
Column Design
COMBINED FORCES
AISC Manual – 16th Edition
ANSI/AISC 360-22
Developed by Scott Civjan
University of Massachusetts, Amherst
Teaching Modules for
Steel Instruction

## Slide 2
Combined Forces:
  Chapter H: Combined Forces
  Chapter C: Direct Analysis Method
  Chapter C: Other Analysis Requirements
  Appendix 7: Alternative Analysis Methods
  Appendix 8: Approximate 2nd Order Analysis
  Chapter B: Local Buckling Classification
  Part 6: Design Tables

## Slide 3
Direct Analysis Method (C1.1) or alternative methods (Appendix 7) may be used, but analysis and design must be consistent with the single approach chosen.
Interaction Equations of Chapter H are applied for member design acceptance. Values used in these equations must be consistent with the analysis and design method used.
Analysis and Design
Combined Forces

## Slide 4
Any rational method that accounts for both P-∆ and P-δ is acceptable.
Second order analysis for LRFD uses load combinations. For ASD, base effects on load combinations times 1.6. Then, divide results by 1.6 to obtain required strengths of components (C2.1(d)).
Analysis and Design
Second order analysis is required per C1.
Combined Forces

## Slide 5
P-δ analysis can be neglected if requirements of Section C2.1(b) are met.
Analysis and Design
Typically, computer analysis is used to calculate second order effects.
Many programs neglect P-δ analysis. Often this is not a significant effect, but it should be checked.
Combined Forces

## Slide 6
This last provision is applicable to the “traditional” method restrictions. Therefore, often requires the application of notional loads in fewer cases than the direct analysis method.
Analysis and Design
Initial imperfections must be considered, either through application of notional loads or direct modeling.
Notional loads are applied to all load cases (Section C2.2b(a)) unless second order to first order drift ratio is ≤ 1.7. Then, can apply notional loads only to gravity load combinations (Section C2-2b(d)).
Combined Forces

## Slide 7
Application of notional loads (Section C2.2b).
Ni = 0.002Yi Equation C2-1
Ni = notional lateral load applied at level i
Yi = gravity load at level i from load combinations
Consider independently in two orthogonal directions.
Combined Forces

## Slide 8
Doubly and Singly Symmetric Members:
  Flexure and Compression

## Slide 9
Combination of multiple states of stress:
Design provisions are simplified and rely on the inherent ductility of steel to redistribute forces throughout the section.
The basic principle for design is an interaction equation which combines forces from axial and bending loads. Shear is checked independently.
Modes of failure from all independent modes are analyzed independently of other modes and forces. This is not completely realistic but is sufficiently accurate for design purposes.

## Slide 10
Equation H1-1b
Equation H1-1a
For
For
Doubly and Singly Symmetric Members:
Flexure and Compression

## Slide 11
Pr = required axial compressive strength from
2nd ORDER ANALYSIS
(from LRFD load combinations).
Pc = available design axial compressive strength
LRFD (strength from Chapter E).
Mr = required flexural strength from
2nd ORDER ANALYSIS
(from LRFD load combinations).
Mc = available design flexural strength
LRFD (strength from Chapter F).
x = strong axis bending
y = weak axis bending
Doubly and Singly Symmetric Members:
Flexure and Compression

## Slide 12
Pr = required axial compressive strength from
2nd ORDER ANALYSIS
(from ASD load combinations).
Pc = allowable axial compressive strength
ASD (strength from Chapter E).
Mr = required flexural strength from
2nd ORDER ANALYSIS
(from ASD load combinations).
Mc = allowable flexural strength
ASD (strength from Chapter F).
Doubly and Singly Symmetric Members:
Flexure and Compression
x = strong axis bending
y = weak axis bending

## Slide 13
For uniaxial bending the interaction equations are depicted above (LRFD).
Uniaxial Flexural Load, Mu
Axial Load Pu
fcPn
fbMn
0.2fcPn
0.9fbMn
Pure axial or flexural load results in strength identical to Chapters E and F.

## Slide 14
Doubly and Singly Symmetric Members:
  Flexure and Tension

## Slide 15
The same equations are used for tension and compression.
(H1-1a and H1-1b)
Substitute:
Pr = required axial tensile strength
(from LRFD load combinations)
Pc = available design axial tensile strength
LRFD (strength from Chapter D)
Additionally, for Mc
Cb can be increased per Section H1.2.
Lateral torsional buckling design strength increases due to tension.
Doubly and Singly Symmetric Members:
Flexure and Tension

## Slide 16
Part 6 of the Manual includes tables that provide the strength for types of member behavior and for all A992 W-shapes.
Compression based on effective length , Lc.
Flexure based on unbraced length , Lb

## Slide 17
Unsymmetric Members:
    Flexure and Compression or Tension
Torsion Combined with Other States of Stress

## Slide 18
  Equation H2-1
fra = required axial stress at point of consideration
Fca = available axial stress at point of consideration
frbw = required flexural stress at point of consideration for major axis bending
Fcbw= available flexural stress at point of consideration for major axis bending
frbz = required flexural stress at point of consideration for minor axis bending
Fcbz = available flexural stress at point of consideration for minor axis bending
Unsymmetric Members:

## Slide 19
When Torsion is included, refer to Section H3.

## Slide 20
  Chapter C:
  Direct Analysis Method

## Slide 21
K = 1 for all design
Second order analysis (P-δ and P-∆) required, such as verified computer analysis or amplified first order analysis.
REQUIRED if ∆2nd Order/∆1st Order > 1.5
(B2 > 1.5) (Section Appendix 7.2.1)
Analysis
Direct Analysis Method

## Slide 22
Direct Analysis Method
Stiffness adjustments are applied to all components that contribute to the stability of the structure (Section C2.3)
Stability is typically affected by flexural stiffness of members in moment frames and axial stiffness of braced frame components.
To simplify analysis, all member stiffnesses can be reduced. This can be accomplished through a reduction in the modulus of Elasticity (E) since flexural and axial stiffness components are functions of EI and EA, respectively.
Reduce Stiffness EI* and EA* per Section C2.3:

## Slide 23
EI* = 0.8tbEI.
Required for all members that contribute to lateral stability of the structure (safe to include for all members).
E = modulus of elasticity
I = moment of inertia about axis of bending
tb = reduction factor for inelastic action
Direct Analysis Method
Reduce Stiffness EI* per Section C2.3:

## Slide 24
Reduce Flexural Stiffness EI* per Section C2.3:
tb = Reduction Factor for Inelastic Action
for
for
Pr = required axial compressive strength
Pns = FyAg for nonslender-element sections
Pns= FyAe for slender-element sections, Ae per Section E7
a = 1.0 (LRFD), 1.6 (ASD)
Direct Analysis Method
Equations C2-2a and C2-2b

## Slide 25
Reduce Flexural Stiffness EI* per Section C2.3:
If an additional notional load of Ni = .001αYi is applied at all levels in all load combinations (even if Section C2.2b(d) applies), τb = 1 per Section C2.3(c).
Therefore, all stiffness could be adjusted similarly.
Direct Analysis Method

## Slide 26
EA* = 0.8EA
E = modulus of elasticity
A = cross-sectional member area
Required for all members that contribute to lateral stability of the structure (safe to include for all members).
Direct Analysis Method
Reduce Stiffness, EA* per Section C2.3:

## Slide 27
  Chapter B:
  Local Buckling Criteria

## Slide 28
Local Buckling
Criteria Defined in Table B4.1
Since members are analyzed independently under flexural and axial loads, the local buckling provisions are checked separately for use in calculations related to each member type.
This does not directly address the combination of stresses which may make web local buckling less likely to occur for some load conditions.

## Slide 29
  Appendix 8:
  Approximate Second-Order Analysis

## Slide 30
Amplified First Order Analysis
Amplification of First-Order Elastic Analysis
This method typically is used in the following situations:
Appendix 8
To analyze and design simple structures being performed by hand calculations.
To verify second order results in computer analyses.
To determine the significance of P-d effects (B1 factor).
Basis for the factors is in 2nd order analysis theory slides.

## Slide 31
Mr = B1Mnt + B2Mlt Equation A-8-1
Mr = second order required flexural strength
B1 = amplification factor to account for second order effects caused by displacements along member length (P-δ effects).
Mnt = first order moment, assuming no lateral translation of frame (from load combinations).
B2 = amplification factor to account for second order effects caused by displacements of member ends (P-∆ effects).
Mlt = first order moment caused by lateral translation of frame (from load combinations).
Amplified First Order Analysis

## Slide 32
Amplified First Order Analysis
Pr = Pnt + B2Plt Equation A-8-2
Pr = second order required axial strength.
Pnt = first order axial force, assuming no lateral translation of frame (from load combinations).
B2 = amplification factor to account for second order effects caused by displacements of member ends (P-∆ effects).
Plt = first order axial force caused by lateral translation of frame (from load combinations).
Notes: 32

## Slide 33
Equation A-8-3
Note that:
in the plane of bending being considered for moment amplification.
Lc1 = Lb or less since there is no end translation.
a=1 for LRFD design
a=1.6 for ASD design
Amplified First Order Analysis

## Slide 34
For cases where loads are present transverse to the member:
Equation C-A-8-2
y and Cm from Table C-A-8.1
For cases where member has end moment only (no transverse loads applied between supports):
Cm = 0.6 - 0.4(M1/M2) Equation A-8-4
M1 = smaller first order end moment
M2 = larger first order end moment
Amplified First Order Analysis

## Slide 35
(largest possible value)
(smallest possible value)
M1
M1
M1
M2=M1
M2=-M1
Amplified First Order Analysis

## Slide 36
or
Note that:
Equation C-A-8-1
in the plane of bending being considered for moment amplification.
K2 ≥ 1 as calculated for end translation.
a=1 for LRFD design
a=1.6 for ASD design
Amplified First Order Analysis
Equations A-8-6 through A-8-8

## Slide 37
Amplified First Order Analysis

## Slide 38
Amplified First Order Analysis
Combined forces will cause Mnt and Mlt in a structure.

## Slide 39
To determine Mnt and Pnt , restrain lateral movement at each story.
Amplified First Order Analysis

## Slide 40
To determine Mnt and Pnt , restrain lateral movement at each story.
Amplified First Order Analysis

## Slide 41
To determine Mnt and Pnt , restrain lateral movement at each story.
Amplified First Order Analysis
Resulting reactions at each story are required to resist the lateral translation of the structure.

## Slide 42
To determine Mnt and Pnt , restrain lateral movement at each story.
Amplified First Order Analysis
Resulting reactions at each story are required to resist the lateral translation of the structure.
Resulting Moments and Axial Forces are Mnt and Pnt respectively.

## Slide 43
To determine Mlt and Plt , apply the resulting reaction at each story.
Amplified First Order Analysis

## Slide 44
To determine Mlt and Plt , apply the resulting reaction at each story.
Amplified First Order Analysis
R3
R2
R1

## Slide 45
To determine Mlt and Plt , apply the resulting reaction at each story.
Amplified First Order Analysis
R3
R2
R1
Resulting moments and axial forces are Mlt and Plt respectively.